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1. PURPOSE
A. The purpose of this policy is to establish the requirements for demarcating Hazardous Locations (HAZLOCs).

B. The purpose of the program is to provide a site-wide consistent demarcation of these HAZLOCs so that all personnel entering a HAZLOC are aware of the Class, Division, and Group they are entering. 

2. SCOPE
A. The Marking of Hazardous Locations (HAZLOCs) Program addresses the following:
2.A.1. Class I HAZLOCs – Flammable gases and vapors
2.A.2. Class II HAZLOCs – Combustible Dusts

3. APPLICATION
A. The Marking of Hazardous Locations (HAZLOCs) Program applies to the following areas:
3.A.1. XXXXXX
3.A.2. XXXXXX
3.A.3. XXXXXX

4. DEFINITIONS

A. Class I, Division 1
A Class I, Division 1 location is a location
(1) In which ignitible concentrations of flammable gases, flammable liquid–produced vapors, or combustible liquid–produced vapors can exist under normal operating conditions, or
(2) In which ignitible concentrations of such flammable gases, flammable liquid–produced vapors, or combustible liquids above their flash points may exist frequently because of repair or maintenance operations or because of leakage, or
(3) In which breakdown or faulty operation of equipment or processes might release ignitible concentrations of flammable gases, flammable liquid–produced vapors, or combustible liquid–produced vapors and might also cause simultaneous failure of electrical equipment in such a way as to directly cause the electrical equipment to become a source of ignition.

B. Class I, Division 2
A Class I, Division 2 location is a location
(1) In which volatile flammable gases, flammable liquid–produced vapors, or combustible liquid–produced vapors are handled, processed, or used, but in which the liquids, vapors, or gases will normally be confined within closed containers or closed systems from which they can escape only in case of accidental rupture or breakdown of such containers or systems or in case of abnormal operation of equipment, or
(2) In which ignitible concentrations of flammable gases, flammable liquid–produced vapors, or combustible liquid–produced vapors are normally prevented by positive mechanical ventilation and which might become hazardous through failure or abnormal operation of the ventilating equipment, or
(3) That is adjacent to a Class I, Division 1 location, and to which ignitible concentrations of flammable gases, flammable liquid–produced vapors, or combustible liquid–produced vapors above their flash points might occasionally be communicated unless such communication is prevented by adequate positive-pressure ventilation from a source of clean air and effective safeguards against ventilation failure are provided.



C. Class II, Division 1 
A Class II, Division 1 location is a location
In which combustible dust is in the air under normal operating conditions in quantities sufficient to produce explosive or ignitible mixtures, or 
(2) Where mechanical failure or abnormal operation of machinery or equipment might cause such explosive or ignitible mixtures to be produced, and might also provide a source of ignition through simultaneous failure of electrical equipment, through operation of protection devices, or from other causes, or 
(3) In which Group E combustible dusts may be present in quantities sufficient to be hazardous.

D. Class II, Division 2
A Class II, Division 2 location is a location
(1) In which combustible dust due to abnormal operations may be present in the air in quantities sufficient to produce explosive or ignitible mixtures; or
(2) Where combustible dust accumulations are present but are normally insufficient to interfere with the normal operation of electrical equipment or other apparatus, but could as a result of infrequent malfunctioning of handling or processing equipment become suspended in
the air; or
(3) In which combustible dust accumulations on, in, or in the vicinity of the electrical equipment could be sufficient to interfere with the safe dissipation of heat from electrical equipment, or could be ignitible by abnormal operation or failure of electrical equipment.


5. REFERENCES
A. NFPA 70, National Electric Code
B. NFPA 497, Recommended Practice for the Classification of Flammable Liquids, Gases, or Vapors and of Hazardous (Classified) Locations for Electrical Installations in Chemical Process Areas
C. NFPA 499, Recommended Practice for the Classification of Combustible Dusts and of Hazardous (Classified) Locations for Electrical Installations in Chemical Process Areas

6. REQUIREMENTS

A. Each Unit where a HAZLOC is present, the Unit management is responsible for demarcating its HAZLOCs, using the colors and markings as defined in this program.

B. Class I and II, Division 1 areas will be marked with a 3” RED stripe painted on the walking/working surface.
6.B.1. The font inside the 3” RED stripe will be WHITE, use a font similar to Arial, and be at least 2” tall.

C. Class I and II, Division 2 areas will be marked with a 3” YELLOW stripe painted on the walking/working surface.
6.C.1. The font inside the 3” YELLOW stripe will be BLACK, use a font similar to Arial, and be at least 2” tall.
D. The Unit is responsible for maintaining these markings and inspecting/auditing these markings at least annually.
6.D.1. Any Management of Change that would cause the area demarcations to CHANGE, must be updated per the MOC.

E. See APPENDIX A for visuals

7. TRAINING
A. PSM System Work Activities
7.A.1. Personnel, including contract employees, assigned to manage, perform, or verify the work activities in HAZLOCs shall be trained in, and demonstrate an understanding of, this procedure.


8. APPENDICES
A. Visual Aids
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APPENDIX A

Visual Aids

DIVISION 1 HAZLOCs

	CLASS I, DIVISION 1, Group D



	CLASS II, DIVISION 1, Group E, F, G


CLASS 1, DIVISION 1, Group D

DIVISION 2 HAZLOCs

	CLASS I, DIVISION 2, GROUP D



	CLASS II, DIVISION 2, GROUP E, F, G
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