## Sheet1
Date | Incident report summary | contributing factors and possible causes | cause category | occupancy (facIlIty usage) | Injury - Qty | Injury - descrIptIon
2008-01-12 | Accidental discharge of 200kg ammonia. | Not indicated. | Not indicated | Arena | 1 | Ammonia exposure
2008-04-27 | After loud ‘bang’ was heard coming from the ‘Ice house,’ the fire department was called and responded to a report of an ammonia odour. A suction surge drum attached to the ice machine weld ‘let go’ and the tank seam opened. | The weld on the 20” x 30” suction surge drum of the ice maker appeared of poor quality leading to a product failure. The system safety valves are old and need replacing. The system pressure did not reach the set point of the safety valves at 150psi. The tank is almost 50 years old and subject to constant pressure cycles. | Equipment failure | Food processing/ production | 0 | NA
2010-03-05 | Approximately 45 to 50 lbs ammonia was released. The facility “lost a condenser pump as it tripped out on high amps.” A pressure relief valve opened and released the ammonia gas through the emergency discharge line. | Not indicated. | Equipment failure | Arena | 0 | NA
2010-04-11 | Brine chiller tube leak which allowed high pressure ammonia to leak into the low pressure brine system. | It was determined that the chiller had an internal fault. | Equipment failure | Arena | 0 | NA
2010-07-17 | Ammonia refrigerant entered a ‘chill room’ at an industrial facility. Corrosion to a 3/8-inch to a 1/4-inch forged steel bushing allowed it to split open and release ammonia. | By design, the bushing had only a small amount of material available to resist pressure. 3/8- to 1/4-inch bushing has threads cut inside and outside to allow use as bushing and when external corrosion worked at the bottom of the outside threads to reduce the already small amount of material (less than 1/8 inch). The working pressure of the ammonia on the low side split open the strainer bushing with the strainer drain valve still attached. Avoiding use of forged steel bushings on the initial installation with thin side walls and also where exposure or corrosion is a possibility. | Installation | Food processing/ production | 0 | NA
2010-10-21 | An ammonia leak occurred in the machinery room of a community ice arena. A pressure relief valve located on the condenser tower of the heat recovery system opened | The plant operator and refrigeration contractor found the condenser motor did not start. With the failure of the condenser motor, the system temperature increased and the pressure rose to its limit (where the pressure relief valve opened). With the failure of this motor, an increase in system temperature and corresponding pressure resulted and rose to the point of causing the pressure relief valve to open. Each compressor is fitted with a high pressure limit that should have opened the circuit to the compressor, before getting to the point of relieving through the pressure relief valve. This did not occur as this safety device failed to operate. As recently as July/August of 2010, they were tested and all but two of the safety switches were replaced. This is one of the two that tested ok. | Equipment failure | Arena | 1 | Ammonia exposure
2010-11-11 | An ammonia leak occurred in the machinery room of an unoccupied arena. An employee was attempting to add oil to an ammonia compressor when he observed a leak (fill hose was not attached). Approximately 200 lbs ammonia was released. | Qualified person was trained, but with minimal experience in this procedure. No written procedure was available, and an error occurred while executing the procedure. The shut-off valve type (wrench-operated, mufti-turn, no position indicator) added complexities to the process. | Operating procedure | Arena | 0 | NA
2010-11-23 | Ammonia was released at a recreational facility. A high pressure cut out switch failed to shut down a compressor when the compressor experienced a high pressure condition. Pressure continued to build until a safety relief device operated releasing ammonia gas to atmosphere via the relief stack, which triggered the ammonia alarm. | The water supply line to the condenser had no protection and was subject to freezing during cold weather. The high limit switch was old (1986) and is mounted on the compressor base subjecting it to vibration. The safety relief operated as designed, venting gas to atmosphere, preventing a possible catastrophic failure. A high-pressure cut-out switch failed to shut down one of the compressors and as a result, a high pressure condition was created. One of four high limit switches failed to shut down its compressor. The high limit switch was old (1986) and is mounted on the compressor base subjecting it to vibration. | Installation | Arena | 0 | NA
2011-10-27 | Employees at an industrial premise observed a leak from the freezer’s evaporator coil. | Corrosion to steel bushing allowed the ammonia to leak in the mechanical room housing the evaporator coils. | Operating procedure | Food processing/ production | 0 | NA
2011-11-12 | An ammonia leak occurred at a commercial-industrial facility. Approximately 10 lbs ammonia entrained in approximately 200 litres of compressor oil was released when a suction side 3/8-inch pressure sensing line failed. The suction side oil pressure pushed approximately 200 litres of oil from the reservoir onto the floor where the entrained ammonia then escaped to atmosphere. | The 3/8-inch stainless steel tubing within the compression fitting failed when a circumferential crack completely fractured. The crack within the 3/8-inch stainless steel compression fitting did not show up on external inspection. Metal fatigue appeared to be a factor, along with unit vibration and initial metal stress within this type of compression joint. The refrigeration contractor identified the main cause and factors leading to the failure as a severe vibration condition of the compressor. This severe vibration condition only occurs when only happens when the control slide valve is at, or at near its minimum position. The vibration was so intense that the contractor immediately shut the compressor down. Also, the contractor’s investigation discovered the ‘PHD’ vibration monitoring system was inactive. When the monitoring system was activated, the compressor in fact shut down on ‘high vibration.’ | Operating procedure | Food processing/ production | 0 | NA
2011-11-28 | Approximately 400lbs ammonia refrigerant was released to atmosphere from a safety valve on the outdoor refrigerant condenser. At shift change, an uncertified operator was made aware that two ammonia refrigeration compressors had been short-cycling from 0400 Hrs (low suction pressure). The operator then opened the suction by-pass valve to a second chiller. Both ammonia compressors started then quickly tripped. The operator reset both high pressure limits. This process was repeated. The ammonia condenser safety valve lifted, and when the operators walked outside to investigate they both walked into ammonia vapor. A third compressor continued to cycle and lift the safety valve for one hour (400 lbs of ammonia released). | Condenser pump controller (Johnson Controls/Penn P70AA-119, J0019, range 50/300 psig, opens low) fails after 6 months of service, causing condenser pump to run continuously. Condenser is subject to adverse ambient conditions (freezing temp/high relative humidity) which causes: 1) ice to deposit on fan blades (tripping fan vsd (sic) on overload), and 2) ammonia migration from HP receiver to condenser (where liquid accumulates in the tubes and restricts hot gas flow, resulting in high back pressure at compressors), and 3) ammonia migration from chiller to high pressure receiver (resulting in low suction pressure at the compressors). Condenser safety valve appears to lift prematurely (less than 250 psi) and does not reset. Operator error due to lack of training and knowledge also contributed. | Equipment failure | Arena | 3 | Ammonia exposure
2011-11-30 | Approximately 300lbs ammonia was released when two maintenance contractors attempted to transfer ammonia from a liquid receiver to a storage bottle. While attempting to purge the transfer hose, the ratchet wrench on the isolation valve failed to operate in the reverse direction. The maintenance contractor inadvertently opened the valve wider, allowing the release of ammonia. | The primary cause of the release was due to a ratchet wrench which failed to operate correctly (i.e., in the opposite direction). | Equipment failure | Arena | 0 | NA
2012-02-28 | Approximately 75 lbs liquid ammonia was released into the machinery room at an industrial facility when a gasket failed on the cap of a liquid level controller for a refrigeration vessel. | Examination of the cap on the liquid level control revealed impact damage. This damage is the result of the occasional physical removal of ice. Over time the cap loosened causing liquid ammonia to leak by the cap gasket. The initial attempt to tighten the cap resulted in fracturing the fibre gasket. Incorrect procedures, inadequate staff training and poor quality control also ontributed. Some written procedures and emergency instructions were in place but not entirely followed. | Operating procedure | Food processing/ production | 0 | NA
2012-07-20 | An ammonia leak occurred at a commercial facility. The leak occurred at the compressor and was isolated by the shut-off valves. | Normal wear and usage on the compressor was observed where the mechanical seal failed. | Equipment failure | Food processing/ production | 0 | NA
2012-09-12 | At a recreational facility, the ammonia LED sensor display indicated 7ppm. An ammonia leak was detected and isolated to the compressor #2 suction valve. | It was reported to the safety officer that the contractor installed the suction valve without securing (tightening) the valve bonnet. In addition, the bolts may not be to specification and may not have been threaded to depth properly at the flange connections to the associated valve piping. | Installation | Arena | 0 | NA
2012-11-04 | Approximately 100lbs ammonia was released into an unoccupied processing room of an industrial facility when a pressure gauge failed on the liquid line to an ammonia evaporator. | Inspection revealed that a second pressure gauge (on the hot gas line for the same installation) was pinned at maximum pressure. Both pressure gauges had a range of 0 to 150psi and were installed in a system with an operating pressure of 150 to 160psi. The pressure gauge failed from over-pressure operation. | Installation | Food processing/ production | 0 | NA
2013-01-18 | The recreational facility’s ammonia alarm sounded when the ammonia concentration was detected at 25ppm. Operators were in the process of topping up the ammonia charge from a portable tank. When threading the flexible hose into the charge line, the port on the valve discharged ammonia and blew the flexible hose away from the fill valve. | The fill line was already open when an operator attempted to connect the portable tank’s flexible hose. Because the line was open, when the operator was threading the flexible hose onto the charge line, the port valve discharged ammonia and blew the flexible hose away. | Operating procedure | Arena | 0 | NA
2013-03-06 | The shift engineer observed that the ammonia leak monitor was in alarm (>35ppm). When the shift engineer activated the control system reset, the system failed. With no condenser fans or pumps in service, the high pressure discharge quickly exceeded the relief valve settings and two relief valves were activated, resulting in approximately 500lbs ammonia released to atmosphere. | “High Liquid Level” in the Low Temp Suction Accumulator (for Frick #1) shuts down all plant equipment (in the main compressor room) via the “control system” (this also shuts down the evaporative condenser fans and water pumps). Frick #2 (in auto control) starts up on local controller call (during the plant “trip”). With no condenser fans or pumps in-service, the high pressure discharge quickly exceeds relief valve settings (250 psi) and two relief valves are activated (one does not reseat).This 1970 vintage plant has had at least two up-grades, and a subsequent investigation identifies control system deficiencies. Lack of knowledge and inadequate staff training contributed. | Equipment failure | Food processing/ production | 0 | NA
2013-05-15 | Approximately 200 lbs ammonia was released to atmosphere from a refrigeration system at an industrial facility when a compressor controller and control system failed. Two of the eight condenser relief valves were activated. | High Liquid Level (in the Low Temp Suction Accumulator) initiated a shutdown of all plant equipment via the plant control system. However, during the investigation it was discovered that the plant control system does not shut down the Frick #2 compressor, and the NH3 liquid pumps, which are associated with the remote “High Temp Air Chill System”. Frick #2 compressor continued to run and, with no condenser fans or water pumps in-service, the condenser pressure quickly exceeded relief valve settings (250 psig). The investigation also revealed the #2 compressor did not trip at the compressor’s local PLC. A pressure transducer would not sent a signal past the equivalent of 190 psig. Poor quality control, inadequate staff training and lack of knowledge also contributed. | Equipment failure | Food processing/ production | 19 | Ammonia exposure
2014-01-17 | A retaining bolt disengaged from the manway door yoke on the oil separator of an ammonia screw compressor. A second retaining bolt remained loosely in place. | Pressure cycles and transmitted compressor vibration resulted in gradual loss of bolt torque and then movement of the bolt in the slotted yoke, until the bolt slipped out of the yoke. An inadequate routine maintenance procedure and lack of knowledge contributed. | Operating procedure | Arena | 0 | NA
2014-07-08 | The fire department responded to the plant’s fire/ammonia alarm. The defrost line to the ice cream room cooler isolation valve failed and the relief valve in the same line also lifted. | There was poor documentation to prove adherence to risk-assessed plant requirements. | Operating procedure | Food processing/ production | 0 | NA
2014-07-30 | An ammonia leak occurred at an industrial facility. An approximately six-inch crack at the fillet weld along the edge of the plate freezer element resulted in approximately 30 to 50lbs of ammonia refrigerant being released to the atmosphere. | The leak occurred on one of the plate elements on plate freezer #3. The plate freezers have horizontal plate elements which can be manually raised or lowered using hydraulic controls. Food product is frozen using the refrigerant filled plate elements. The plate freezer elements were moved using hydraulics with no product to freeze between the plates. Excessive forces on the plate elements caused an approximately six-inch crack at the fillet weld along the plate edge. As a result ammonia refrigerant was released into the atmosphere. The hydraulics are operated manually and have no limit switches. Personnel operating the equipment were given instructions that were not clear enough or misunderstood. The plate freezers are designed to have fish in between them when being operated into the freezing position. | Operating procedure | Food processing/ production | 0 | NA
2014-08-22 | Approximately 200 lbs ammonia was released to atmosphere. The condenser safety valve activated due to ‘no cooling’ in the condenser while the ammonia compressor was operating. | While restarting the plant after a power failure, the operator forgot to start the condenser circulating pump (which should be started before starting the compressor). The compressor was started without condenser cooling, and as a result, ammonia gas temperature began to rise, thus raising the gas pressure in the system. Eventually the gas pressure rose more than the safety valve setting, activating the safety valve which released the ammonia to atmosphere.The compressor’s high pressure safety cut off did not activate. The high pressure cut off is supposed to activate and shut off the compressor unit when the system senses a high pressure condition. | Equipment failure | Food processing/ production | 0 | NA
2014-08-22 | While in the process of adding oil to a compressor, an employee was sprayed in the abdomen with some oil from the compressor. Upon smelling ammonia, he immediately left the area and activated the ventilation system on the way out. He left the valve to the compressor open and it continued to spray out the remaining oil. The compressor was off but some ammonia escaped into the room. | The operator thought he had turned the valve off before he proceeded to remove the connecting oil hose; he had not. In fact, he indicated that the direction he turned the valve caused it to become more open. | Operating procedure | Arena | 1 | Ammonia exposure
2014-08-30 | An ammonia leak occurred at a fish production facility. During normal operation at the production facility, a 1/4-inch pipe fitting broke off a liquid ammonia pipe line in the glaze freezer. | The glaze freezer is a large room (approximately 60 feet x 60 feet x 18 feet high). The overhead liquid ammonia line is located approximately four feet below the ceiling of the glaze freezer. The forklift operator raised a basket too high and broke a 1/4-inch fitting off the ammonia pipe line. | Operating procedure | Food processing/ production | 0 | NA
2014-10-06 | Ammonia was released from Compressor Nylon #4 mechanical seal. The shaft seal ring let go from deterioration, allowing oil and ammonia to leak. | The deterioration over time in normal operating conditions. | Equipment failure | Food processing/ production | 0 | NA
2014-10-06 | Approximately 300lbs ammonia was released to atmosphere at a recreational premise (arena). The plant was allowed to run to cool the ice surface down prior to commencing with the installation of pipe fittings on the glycol line for the compressors. Two high pressure excursions were created when the faulty high side float was put in auto mode. The high side float was manually operated in the open position prior to the release because it was prone to getting stuck in the closed position. Evidence suggests that the second high pressure excursion never reached the 250psig set pressure of the condenser pressure relief valve and that the valve lifted early. The two compressors had to be manually shutdown upon discovery of the release as the high pressure limit never tripped. A crack on a threaded pipe joint on the pressure relief discharge piping allowed a portion of the refrigerant to be released adjacent to the condenser, approximately 20 feet below the normal stack discharge height. The northerly wind caused some of the refrigerant to concentrate near the north end of the building where air intakes to the building are located. | A faulty high side float caused the two high pressure excursions. An overdue pressure relief valve replacement interval and an installation in the wrong orientation may have contributed to the early release. The lower discharge point and the northerly wind could have resulted in more of the ammonia being concentrated on the north end of the building where the air intakes are located. | Equipment failure | Arena | 3 | Ammonia exposure
2014-10-30 | A release of approximately 25lbs ammonia vapours occurred at a poultry processing plant. The ammonia vapour was released when hot gas ammonia piping in the packaging room ruptured. | The hot gas ammonia piping that failed was constructed of NPS 3/4 schedule 80 carbon steel material. This piping was supported by a pipe hanger constructed of stainless steel material. The piping was uninsulated and was in direct contact with the hanger. | Installation | Food processing/ production | 1 | Ammonia exposure
Extensive pitting on the external surface of the carbon steel piping occurred adjacent to the contact surface of stainless steel pipe hanger. The packaging room, where this piping is located, had a cold and moist environment. The external pitting of the piping was caused by the galvanic corrosion of two dissimilar metals (carbon steel piping and stainless steel pipe hanger) over a period of time in presence of moisture. The external pitting reduced the wall thickness of the hot gas ammonia piping which caused the weakening and eventual failure. The root cause was determined to be the incorrect selection of pipe hanger material for the plant environmental condition. The ineffective inspection and maintenance program were the contributing factors.
2014-11-05 | A chemical analysis report indicated ammonia was present in the system’s brine solution. | Not indicated | Not indicated | Arena | 0 | NA
2014-11-10 | Approximately 75lbs ammonia was released to atmosphere. An operator turned on the Mycom 200 compressor and a smell of ammonia was detected on the outside of the building soon after. No significant ammonia smell was detected inside the mechanical room by the operator. The compressor was immediately shutdown to stop additional ammonia from escaping. The release was blamed on the pressure relief valve on the Mycom 200 compressor economizer lifting and releasing ammonia out the pressure relief discharge stack on the roof. The pressures noted on the compressor during the incident were within normal operating ranges (131psig). The compressor operating limit, high pressure limit switch (190psig) and the common high pressure limit switch (200psig) were never activated during the incident. | The pressure relief valve was tested. The valve leaked heavily during the pre-test but still popped at its set pressure of 250psig. The valve was within the required 5yr replacement interval. Since the pressure relief valve lifted as designed it can be concluded that the pressure exceeded the set pressure of the operating limit and the two high pressure limits. None of the devices caused a shutdown of the compressor. No records of annual testing and calibration of these devices could be provided as required by CSA B-52-13, 8.4.2. A corroded and leaking pipe cap was found on the drip leg of the pressure relief discharge piping following the incident. Condensation trapped at the bottom of the drip leg was blamed for the corrosion. The seal on the flapper on the discharge stack may have contributed to the water accumulation. Inadequate supports and heavy external corrosion was noted on the pressure relief discharge piping above the roof. | Operating procedure | Food processing/ production | 0 | NA
2014-11-28 | Between Nov 28, 2014 and Dec 1, 2014, approximately 2,000 lbs ammonia was released to atmosphere due to a leaking pressure relief valve at a food production facility. There were no visible signs of ammonia leakage although there was a strong odour of ammonia reported. An employee noticed that the motor overload alarm on #3 compressor was triggered and the control panel indicated that the spray pump was in the OFF position. | The refrigeration plant consists of four Vilter refrigeration compressors. Two compressors are operated and the third compressor remains on standby. The #4 compressor is rarely operated, but the discharge valve is left open as there is a check valve in the system. On Friday, November 28th, 2014 #2 & #3 compressors were operating and #1 compressor was on standby. The condenser spray pump switch has three positions: AUTO, OFF and MANUAL. This switch is always kept in AUTO position, but during the owner’s investigation it was found to be in the OFF position, which led to high system pressures due to lack of cooling medium in the condenser. This pressure excursion triggered #1 and #2 compressors high pressure safety causing the running #2 compressor to trip and rendering #1 compressor inoperative. #3 compressor high pressure switch did not trip at the set pressure of 220 psi, eventually the #3 compressor motor tripped on overload. This resulted in the pressure relief valve lifting (set pressure: 250 psig) on suction accumulator oil pot on #4 compressor through the leaking check valve. When the condenser spray pump was put in AUTO position, the system pressures returned to normal but the pressure relief valve on #4 compressor suction accumulator oil pot did not re-set and kept leaking. The refrigeration system operating pressures fluctuates depending on the production or cleaning cycles. The system pressures are higher during the ‘Cleaning in Place’ cycle on evaporators. Depending on the pressures, the leaking pressure relief valve was discharging varying amount of ammonia, leading to varying odour intensities over the last few days. Most ammonia was discharged November 30 while performing ‘Cleaning in Place’ on production line 2 & 3. All high pressure switches were tested by the licensed contractor and #3 compressor high pressure was found to be tripping at 280 psi as opposed to the set pressure of 220 psi. This faulty high pressure switch was 6 months old and made by Johnson Control. The other high pressure switches (#1, #2 & #4 compressors) tripped at the individual set pressures. The root cause of the ammonia release was determined to be faulty high pressure switch installed on #3 compressor. The leaky pressure relief valve contributed to the release of ammonia. The ineffective operation and alarm system were the other contributing factors of the incident. | Equipment failure | Food processing/ production | 0 | NA
2015-02-17 | Ammonia leaked from the blast freezer refrigeration system at a poultry processing plant. | The blast freezer is located in the main freezer and has restricted access. Personnel enter the freezer once a day to load and unload the poultry. This blast freezer is operated off the low-temperature liquid receiver (the system normally operates under negative pressure) located in the machinery room. During planned servicing of the low-side compressor, the three-hour downtime resulted in system pressure becoming positive. The initial installation of the low temperature suction piping resulted in isalignment and eventual leak through the gasket. Normal wear-and-tear, inadequate procedure and ineffective inspection and testing were contributing factors. | Installation | Food processing/ production | 0 | NA
2015-04-21 | "A leak on the south coil of the ammonia plan evaporative condenser was discovered. The operators isolated the coil and proceeded to bleed the remaining ammonia from it. Several attempts were made to bleed to atmosphere at the coil outlet. The first attempt was conducted for approximately 30 minutes. As a result of this controlled release, ammonia was drawn into the fresh air intake of the arena change room air-handling system approximately 27 feet away. A second attempt to bleed the coil was made, this time to water, for about 15 minutes. This attempt was stopped due to the strong ammonia odour. A third attempt was made to bleed the coil by attaching a hose to a pole approximately four feet above the roof line, next to the ammonia vent stack. After this attempt, an ammonia odour was detected by people on an adjacent street. An operator sustained injuries to his mouth while disposing of the water-ammonia mixture (created by the second attempt to bleed the coil). The operator attempted to siphon the mixture via a hose. While initiating the siphon, the mixture entered and burned his mouth. | Not indicated | Not recorded | Arena | 1 | Burns in the mouth from ammonia-water mixture
2015-05-07 | Less than one pound of ammonia was released from a leak on the low-pressure control on Compressor #2. | Low-pressure pressure switch diaphragm failure on the compressor. | Equipment failure | Arena | 0 | NA
2015-06-11 | A technician was bleeding (purging) an ammonia line outside of the arena building adjacent to the condenser. Ammonia vapours entered the building, exposing three people to ammonia vapours. | An ammonia-rated half-inch diameter hose was attached to the piping connection and ammonia vapours were allowed to escape through the hose into two 45-gallon drums filled with cold water. The containers were not covered when the refrigeration line was purged. | Operating procedure | Arena | 3 | Exposure to ammonia vapour
2015-07-28 | Approximately half a kilogram of ammonia was released to atmosphere due to a leak in the hot gas strainer gasket. | The cold room was operating in warmer temperatures than normal and an employee found the hot gas timer stuck in the 'ON' position, leaving the hot gas line charged with 140-150 psi ammonia gas for an unknown period of time. This condition caused the deteriorated gasket in the strainer on the hot gas defrost line to fail and start leaking liquid ammonia. | Operations | Food processing/ production | 0 | NA
2015-09-10 | The threaded fitting connecting the tubing line to a pressure switch became loose, which allowed ammonia gas to enter the machine room, triggering the leak detection system. | Not indicated | Not recorded | Arena | 0 | NA
2015-09-20 | Approximately 140 pounds of ammonia was released to atmosphere. The fill valve was not closed completely after adding oil to the compressor. The pressure inside the compressor pushed out oil and ammonia refrigerant. An operator was taken to hospital for exposure to ammonia vapours. | The facility did not have a procedure in place for adding oil to the compressors. As a result, isolation of the line was not confirmed prior to disconnecting the hose fittings. | Operating procedure | Arena | 1 | Exposure to ammonia vapour
2015-09-24 | Approximately 200 pounds of ammonia was released into a cold storage area at a food and beverage producing facility. An operator dropped a heavy line onto the valve (fitting) of an ammonia oil drain, causing it to crack and release ammonia. | The fitting was an ammonia oil drain line on an evaporator surge drum. The oil drain piping and valve were exposed and susceptible to damage. | Installation | Food processing/ production | 0 | NA
2015-11-04 | Approximately half a pound of ammonia was released outdoors at a food processing facility. During a routine maintenance procedure, an unplanned high pressure condition resulted in the activation of the relief valve on a pressure vessel (oil pot). | The employee was draining the oil, which is a routine maintenance procedure. As the isolated oil pot (pressure vessel) warmed up the liquid ammonia, it vapourized, causing the pressure to rise until the relief valve lifted. The employee was not following the current procedure, and the procedure used had inaccuracies. | Operating procedure | Food processing/ production | 0 | NA