## Slide 1
GRAND RAPIDS, MICHIGAN
International Fire Code 2021
Flammable Liquids
Applicable Code Sections
City of Grand Rapids | Chapter 159 – Fire Prevention | Ord. No. 2024-01
IFC Chapters 50 & 57

## Slide 2
PRESENTATION OVERVIEW
01
Code Adoption
Grand Rapids adoption of IFC 2021 – Sec. 9.331
02
Hazardous Materials – General
Chapter 50: Scope, piping, tanks, safety precautions
03
Use, Dispensing & Handling
Section 5005: Indoor/outdoor operations & limit controls
04
Flammable Liquids (Ch. 57)
Fire protection, labeling, piping systems & site assessment
05
Liquid Transfer Operations
Section 5705: Pumps, pressurized systems, bonding requirements
06
Tank Vehicle Operations
Section 5706: Tank requirements, venting, location restrictions

## Slide 3
CODE ADOPTION – SEC. 9.331
ORDINANCE HISTORY
Ord. No. 2006-36
June 13, 2006 – Original adoption
Ord. No. 2014-24
May 13, 2014 – Amendment
Ord. No. 2018-58
Sept. 18, 2018 – Amendment
Ord. No. 2024-01
Jan. 9, 2024 – Current revision (IFC 2021)
KEY CODE PROVISIONS
Adopts IFC 2021 edition with Appendices B, D, F, I, J, and N
Prescribes minimum requirements for life and property safety
Governs storage, handling, and use of hazardous materials
Addresses conditions hazardous to life related to building occupancy

## Slide 4
CH. 50 – HAZARDOUS MATERIALS: GENERAL PROVISIONS
§5001.1 Scope
Covers prevention, control & mitigation of dangerous conditions
Applies to storage, dispensing, use, and handling
Where specific chapter requirements exist, those take precedence
All hazards must be addressed for multi-hazard materials
§5003.2 – Piping & Tanks
Must comply with ASME B31.1 or approved standards
Piping labeled per ASME A13.1
Manual or remote fail-safe shutoff valves required
Backflow prevention is required where backflow creates a hazard
Above-ground tanks: location per outdoor storage requirements
§5003.5–5003.9 Safety
NFPA 704 hazard signs on all stationary containers & tanks
No smoking within 25’ of outdoor storage areas
Personnel must be trained on the chemical nature & emergency actions
Fire dept. liaison must be designated & trained
Static charge prevention required in flammable operations

## Slide 5
§5003.12 – OUTDOOR CONTROL AREAS
GENERAL REQUIREMENTS
Keep free of weeds, debris, and combustibles not needed for storage
15 ft clearance of combustibles around the control area
Located ≥20 ft from public street, alley, or lot line
15 ft
Combustible clearance around control area
20 ft
Min. from public street/alley/lot line
50 ft
Separation between 2-area groups
300 ft
Separation between groups (>35k sq ft)

## Slide 6
§5005 – USE, DISPENSING & HANDLING
Limit Controls Required
High-liquid-level control on open tanks to prevent overfill
Low-liquid-level safeguards to prevent overheating
Temperature control per §5004.8.1
Pressure control per §5004.8.2
Power & Monitoring
Standby/emergency power for ventilation, treatment, temperature & alarm systems
Exempt if approved fail-safe system installed
Alarm & detection systems must be electrically supervised
Audible & visual signal at constantly attended location
Outdoor Dispensing (§5005.3)
Spill control for closed systems: >55 gallons
Secondary containment for closed systems: individual >55 gal or multiple >1,000 gal
30 ft clearance from combustibles around outdoor dispensing area
Overhead noncombustible shelter does not convert to 'indoor use' if built per IBC weather protection requirements
Adequate lighting (natural or artificial) required at all times

## Slide 7
CHAPTER 57 – FLAMMABLE LIQUIDS: FIRE PROTECTION & LABELING
§5703.2
Fire Protection
Fire protection per Chapter 9 for all storage, use, dispensing & handling
Portable fire extinguishers per Section 906
Hose lines per Section 905
§5703.3
Site Assessment
Required upon spill, leak or discharge from tank system
Completed & submitted to fire dept. within ≤60 days
Conducted to identify fire/explosion hazards
§5703.5
Labeling & Signage
Fire code official may require warning signs
Signs: white lettering on RED background
Text: 'DANGER—FLAMMABLE LIQUIDS'
Min. 3 in. letter height, ½ in. stroke width
Piping labeled per ASME A13.1
§5703.4
Spill Control
Required where MAQ per control area is exceeded
Applies to Class I, II and IIIA liquid areas
Spill control + secondary containment per §5004.2

## Slide 8
§5703.6 – PIPING SYSTEMS FOR FLAMMABLE LIQUIDS
§6.2
Design & Fabrication
Per applicable standard in Table 5703.6.2 and NFPA 30 Chapter 27. NOTE: ASME B31.3 is the applicable pipe code for this set-up.
§6.3
Testing
Hydrostatically tested to 150% of max anticipated pressure, or pneumatically to 110% (min. 5 psig). Maintained for visual inspection; no leakage/distortion for ≥10 minutes.
§6.4
Vehicle Protection
Guard posts or approved means required to protect piping, valves, and fittings from vehicular damage per §312.
§6.6
Valves
Sufficient manual control & check valves for normal & emergency operation, including pump piping systems.
§6.7
Connections
Above-ground tanks with below-liquid-level connections require internal or external isolation valves as close as practical to the tank shell.
§6.8
Piping Supports
Substantially supported; protected from fire by draining (≥1% slope), 2-hr fire-resistance rating, or other approved method.
§6.10
Pipe Joints
Must be liquid tight: welded, flanged, or threaded. Class I liquid joints in concealed spaces within buildings must be welded.

## Slide 9
§5705 – DISPENSING, USE, MIXING & HANDLING
§5705.2.4 – Approved Transfer Methods
(Class I, II & III Liquids)
From safety cans complying with UL 30
Through an approved closed piping system
By the approved pump taking suction through the top opening
By gravity (Class IB, IC, II & III only) via self-closing valve with spill control & secondary containment
Class IA liquids: NOT dispensed by gravity from tanks
Approved engineered liquid transfer systems
  Exception: Original containers ≤5.3 gallons
§5705.2.5 – Static Bonding (Manual Filling)
Class I liquids must NOT be transferred without electrical interconnection of nozzle and container
Acceptable: Metallic floor plates electrically connected to fill stem
Acceptable: Bond wire connecting fill stem to container during filling
§5705.2.1–2 – Pumps & Pressurized Systems
Positive-displacement pumps: must have pressure relief or interlock to prevent over-pressure
Only inert gases used for pressure transfer of Class I liquids
Controls & pressure relief to prevent exceeding max working pressure
Air or oxygen NOT permitted for pressurization

## Slide 10
§5706.2 – PERMANENT & TEMPORARY ABOVE-GROUND TANKS
1,100 gal
Max for PERMANENT above-ground tanks
(Class I or II liquids)
10,000 gal
Max for TEMPORARY above-ground tanks
(Class I or II liquids)
50 ft
Min. distance from buildings and
combustible storage
§5706.2.4.1 Fill Opening Security
Fill openings must have a locking closure device
Fill openings must be separate from vent openings
§5706.2.4.2 Venting
Normal venting per §5704.2.7.3
Emergency venting per §5704.2.7.4
Emergency vents must prevent localized overheating or flame impingement on tank
§5706.2.4.3 Location
Tanks kept outside (not inside buildings)
Min. 50 ft from buildings & combustible storage
Vehicles being filled must also remain ≥50 ft from structures or haystacks
§5706.2.4.4 Prohibited Locations
Storage of Class I and II liquids in above-ground tanks is prohibited in designated restricted districts per local law

## Slide 11
KEY COMPLIANCE TAKEAWAYS
IFC 2021 – Flammable Liquids Compliance Summary
Piping
ASME B31.3 governs. Test to 150% hydrostatic or 110% pneumatic (min. 5 psig, ≥10 min).
Signage
NFPA 704 hazard ID on all containers. 'DANGER—FLAMMABLE LIQUIDS' in white on red.
Static Control
All manual Class I liquid filling requires a bonded/grounded electrical interconnection.
Tanks
Permanent tanks ≤1,100 gal; Temporary ≤10,000 gal; Keep ≥50 ft from structures.
Spill/Containment
Required when MAQ exceeded. Outdoor: open systems >1.3 gal; closed >55 gal.
Site Assessment
Mandatory for any spill/leak from tank system; submit to fire dept. within 60 days.
Grand Rapids, Michigan • Chapter 159 – Fire Prevention • IFC 2021 Edition
Ord. No. 2024-01 • Effective January 9, 2024